## locations
dbo.section | dbo.entity_name | dbo.type | dbo.id | dbo.connections.contains
Buildings | IN-BLR-ANANTA | FACILITIES/BUILDING | d9fd1270-218c-4998-ab93-c7be5bd22f31
Floors | IN-BLR-ANANTA-2 | FACILITIES/FLOOR | 28ed1456-9605-452d-8caf-164ddc4a7081 | IN-BLR-ANANTA
Rooms | IN-BLR-ANANTA-2-1ELECRM | FACILITIES/ROOM | ece78ab4-747d-42f3-8594-6081c1481319 | IN-BLR-ANANTA-2

## assets
entity_instance_name | udmi.version | udmi.device_version | udmi.timestamp | udmi.system.location.site | udmi.system.location.section | udmi.cloud.connection | udmi.gateway.gateway_id | udmi.gateway.proxy_ids | udmi.system.location.position.y | udmi.system.location.position.z | udmi.physical_tag.asset.guid | udmi.physical_tag.asset.site | udmi.physical_tag.asset.name | udmi.pointset.points | udmi.cloud.auth_type | udmi.bacnet_addr | dbo.devices_or_virtual_devices | dbo.type | dbo.connections.feeds | dbo.connections.controls | dbo.links | dbo.links.points | Location | Reporting Device | dbo.cloud_device_id
DDC-18 | 1.4.2 | 1.4.2 | 2024-11-01T09:53:18Z | IN-BLR-ANANTA | IN-BLR-ANANTA-2 | GATEWAY |  | BTU-12,WLD-14,AHU-23,AHU-24 |  |  | 1e6add8b-10ad-4130-ba21-7d920468931b | IN-BLR-ANANTA | DDC-18 | DDC-18 | RS256_X509 | 11036
BTU-12 | 1.4.2 | 1.4.2 | 2024-11-01T09:53:18Z | IN-BLR-ANANTA | IN-BLR-ANANTA-2 | PROXIED | DDC-18 |  |  |  | ee745644-a1c7-4398-aae8-04125bb0d16d | IN-BLR-ANANTA | BTU-12 | BTU-12 |  | 11036 | Device | METERS/HM_CHW_WAC | [6 empty] | 123455627
WLD-14 | 1.4.2 | 1.4.2 | 2024-11-01T09:53:18Z | IN-BLR-ANANTA | IN-BLR-ANANTA-2 | PROXIED | DDC-18 |  |  |  | 8d139527-67b4-473f-a958-7ffd470139b9 | IN-BLR-ANANTA | WLD-14 | WLD-14 |  | 11261 | Device | SAFETY/LDS_WLDS | [6 empty] | 123445667
AHU-23 | 1.4.2 | 1.4.2 | 2024-11-01T09:53:18Z | IN-BLR-ANANTA | IN-BLR-ANANTA-2 | PROXIED | DDC-18 |  |  |  | b9c0a842-d7f7-45a2-996c-8623ed928ba6 | IN-BLR-ANANTA | AHU-23 | AHU-23 |  | 11036 | Device | HVAC/AHU_SFSS4X_ECON_SFVSC4X_CHWRC_SSPC_FDPSM | [6 empty] | 123411267
AHU-24 | 1.4.2 | 1.4.2 | 2024-11-01T09:53:18Z | IN-BLR-ANANTA | IN-BLR-ANANTA-2 | PROXIED | DDC-18 |  |  |  | c86faeaf-58db-4c79-ad6c-aaff54614cfd | IN-BLR-ANANTA | AHU-24 | AHU-24 |  | 11036 | Device | HVAC/AHU_SFSS4X_ECON_SFVSC4X_CHWRC_SSPC_FDPSM | [6 empty] | 123457667

## device_entities
points_type | udmi.pointset.points | udmi.pointset.ref | udmi.pointset.units | dbo.states | dbo.translation.fields | dbo.translation.units | dbo.abstracts | dbo.flag
BTU-12 | cooling_thermal_energy_accumulator | AV314 | megawatt_hours |  | cooling_thermal_energy_accumulator | megawatt_hours: megawatt_hours |  | N
BTU-12 | chilled_supply_water_temperature_sensor | AV317 | degrees_celsius |  | chilled_supply_water_temperature_sensor | degrees_celsius: degrees_celsius |  | N
BTU-12 | chilled_return_water_temperature_sensor | AV318 | degrees_celsius |  | chilled_return_water_temperature_sensor | degrees_celsius: degrees_celsius |  | N
BTU-12 | cooling_thermal_power_sensor | AV347 | kilowatts |  | cooling_thermal_power_sensor | kilowatts: kilowatts |  | N
BTU-12 | chilled_water_flowrate_sensor | AV348 | cubic_meters |  | chilled_water_flowrate_sensor | cubic_meters_per_hour: cubic_meters_per_hour |  | N
BTU-12 | water_volume_accumulator | AV350 | cubic_meters_per_hour |  | water_volume_accumulator | cubic_meters: cubic_meters |  | N
WLD-14 | water_leak_detection_alarm | BI1 |  | 1=ACTIVE 0=INACTIVE | water_leak_detection_alarm |  |  | N
AHU-23 | chilled_water_valve_percentage_command | AV37 | percent |  | chilled_water_valve_percentage_command | percent: percent |  | N
AHU-23 | chilled_water_valve_percentage_sensor | AV38 | percent |  | chilled_water_valve_percentage_sensor | percent: percent |  | N
AHU-23 | leaving_cooling_coil_temperature_sensor | AV39 | degrees_celsius |  | leaving_cooling_coil_temperature_sensor | degrees_celsius: degrees_celsius |  | N
AHU-23 | supply_fan_current_sensor_1 | AV40 | amperes |  | supply_fan_current_sensor_1 | amperes: amperes |  | N
AHU-23 | supply_fan_energy_accumulator_1 | AV41 | kilowatt_hours |  | supply_fan_energy_accumulator_1 | kilowatt_hours: kilowatt_hours |  | N
AHU-23 | supply_fan_power_sensor_1 | AV42 | kilowatts |  | supply_fan_power_sensor_1 | kilowatts: kilowatts |  | N
AHU-23 | supply_fan_run_time_accumulator_1 | AV43 | hours |  | supply_fan_run_time_accumulator_1 | hours: hours |  | N
AHU-23 | supply_fan_rotationalvelocity_sensor_1 | AV44 | revolutions_per_minute |  | supply_fan_rotationalvelocity_sensor_1 | revolutions_per_minute: revolutions_per_minute |  | N
AHU-23 | supply_fan_voltage_sensor_1 | AV45 | volts |  | supply_fan_voltage_sensor_1 | volts: volts |  | N
AHU-23 | supply_fan_current_sensor_2 | AV46 | amperes |  | supply_fan_current_sensor_2 | amperes: amperes |  | N
AHU-23 | supply_fan_energy_accumulator_2 | AV47 | kilowatt_hours |  | supply_fan_energy_accumulator_2 | kilowatt_hours: kilowatt_hours |  | N
AHU-23 | supply_fan_power_sensor_2 | AV48 | kilowatts |  | supply_fan_power_sensor_2 | kilowatts: kilowatts |  | N
AHU-23 | supply_fan_run_time_accumulator_2 | AV49 | hours |  | supply_fan_run_time_accumulator_2 | hours: hours |  | N
AHU-23 | supply_fan_rotationalvelocity_sensor_2 | AV50 | revolutions_per_minute |  | supply_fan_rotationalvelocity_sensor_2 | revolutions_per_minute: revolutions_per_minute |  | N
AHU-23 | supply_fan_voltage_sensor_2 | AV51 | volts |  | supply_fan_voltage_sensor_2 | volts: volts |  | N
AHU-23 | supply_fan_current_sensor_3 | AV52 | amperes |  | supply_fan_current_sensor_3 | amperes: amperes |  | N
AHU-23 | supply_fan_energy_accumulator_3 | AV53 | kilowatt_hours |  | supply_fan_energy_accumulator_3 | kilowatt_hours: kilowatt_hours |  | N
AHU-23 | supply_fan_power_sensor_3 | AV54 | kilowatts |  | supply_fan_power_sensor_3 | kilowatts: kilowatts |  | N
AHU-23 | supply_fan_run_time_accumulator_3 | AV55 | hours |  | supply_fan_run_time_accumulator_3 | hours: hours |  | N
AHU-23 | supply_fan_rotationalvelocity_sensor_3 | AV56 | revolutions_per_minute |  | supply_fan_rotationalvelocity_sensor_3 | revolutions_per_minute: revolutions_per_minute |  | N
AHU-23 | supply_fan_voltage_sensor_3 | AV57 | volts |  | supply_fan_voltage_sensor_3 | volts: volts |  | N
AHU-23 | supply_fan_current_sensor_4 | AV58 | amperes |  | supply_fan_current_sensor_4 | amperes: amperes |  | N
AHU-23 | supply_fan_energy_accumulator_4 | AV59 | kilowatt_hours |  | supply_fan_energy_accumulator_4 | kilowatt_hours: kilowatt_hours |  | N
AHU-23 | supply_fan_power_sensor_4 | AV60 | kilowatts |  | supply_fan_power_sensor_4 | kilowatts: kilowatts |  | N
AHU-23 | supply_fan_run_time_accumulator_4 | AV61 | hours |  | supply_fan_run_time_accumulator_4 | hours: hours |  | N
AHU-23 | supply_fan_rotationalvelocity_sensor_4 | AV62 | revolutions_per_minute |  | supply_fan_rotationalvelocity_sensor_4 | revolutions_per_minute: revolutions_per_minute |  | N
AHU-23 | supply_fan_voltage_sensor_4 | AV63 | volts |  | supply_fan_voltage_sensor_4 | volts: volts |  | N
AHU-23 | return_air_relative_humidity_sensor | AV111 | percent_relative_humidity |  | return_air_relative_humidity_sensor | percent_relative_humidity: percent_relative_humidity |  | N
AHU-23 | return_air_temperature_sensor | AV3 | degrees_celsius |  | return_air_temperature_sensor | degrees_celsius: degrees_celsius |  | N
AHU-23 | supply_fan_speed_percentage_command | AV109 | percent |  |  |  |  | N
AHU-23 | supply_air_static_pressure_sensor | AV26 | pascals |  | supply_air_static_pressure_sensor | pascals: pascals |  | N
AHU-23 | supply_fan_run_status_1 | BV10 |  | 1=ON 0=OFF | supply_fan_run_status_1 |  |  | N
AHU-23 | supply_fan_run_status_2 | BV13 |  | 1=ON 0=OFF | supply_fan_run_status_2 |  |  | N
AHU-23 | supply_fan_run_status_3 | BV16 |  | 1=ON 0=OFF | supply_fan_run_status_3 |  |  | N
AHU-23 | supply_fan_run_status_4 | BV37 |  | 1=ON 0=OFF | supply_fan_run_status_4 |  |  | N
AHU-23 | filter_differential_pressure_status | BV2 |  | 1=PRESENT 0=ABSENT | filter_differential_pressure_status |  |  | N
AHU-23 | return_air_temperature_setpoint | AV12 | degrees_celsius |  | return_air_temperature_setpoint | degrees_celsius: degrees_celsius |  | N
AHU-23 | supply_air_static_pressure_setpoint | AV11 | pascals |  | supply_air_static_pressure_setpoint | pascals: pascals |  | N
AHU-23 | supply_fan_speed_percentage_command |  | percent |  | supply_fan_speed_percentage_command_1 | percent: percent |  | N
AHU-23 | supply_fan_speed_percentage_command |  | percent |  | supply_fan_speed_percentage_command_2 | percent: percent |  | N
AHU-23 | supply_fan_speed_percentage_command |  | percent |  | supply_fan_speed_percentage_command_3 | percent: percent |  | N
AHU-23 | supply_fan_speed_percentage_command |  | percent |  | supply_fan_speed_percentage_command_4 | percent: percent |  | N
AHU-23 | supply_fan_run_command_1 |  |  | 1=ON 0=OFF | supply_fan_run_command_1 |  |  | Y
AHU-23 | supply_fan_run_command_2 |  |  | 1=ON 0=OFF | supply_fan_run_command_2 |  |  | Y
AHU-23 | supply_fan_run_command_3 |  |  | 1=ON 0=OFF | supply_fan_run_command_3 |  |  | Y
AHU-23 | supply_fan_run_command_4 |  |  | 1=ON 0=OFF | supply_fan_run_command_4 |  |  | Y
AHU-24 | chilled_water_valve_percentage_command | AV71 | percent |  | chilled_water_valve_percentage_command | percent: percent |  | N
AHU-24 | chilled_water_valve_percentage_sensor | AV72 | percent |  | chilled_water_valve_percentage_sensor | percent: percent |  | N
AHU-24 | leaving_cooling_coil_temperature_sensor | AV73 | degrees_celsius |  | leaving_cooling_coil_temperature_sensor | degrees_celsius: degrees_celsius |  | N
AHU-24 | supply_fan_current_sensor_1 | AV74 | amperes |  | supply_fan_current_sensor_1 | amperes: amperes |  | N
AHU-24 | supply_fan_energy_accumulator_1 | AV75 | kilowatt_hours |  | supply_fan_energy_accumulator_1 | kilowatt_hours: kilowatt_hours |  | N
AHU-24 | supply_fan_power_sensor_1 | AV76 | kilowatts |  | supply_fan_power_sensor_1 | kilowatts: kilowatts |  | N
AHU-24 | supply_fan_run_time_accumulator_1 | AV77 | hours |  | supply_fan_run_time_accumulator_1 | hours: hours |  | N
AHU-24 | supply_fan_rotationalvelocity_sensor_1 | AV78 | revolutions_per_minute |  | supply_fan_rotationalvelocity_sensor_1 | revolutions_per_minute: revolutions_per_minute |  | N
AHU-24 | supply_fan_voltage_sensor_1 | AV79 | volts |  | supply_fan_voltage_sensor_1 | volts: volts |  | N
AHU-24 | supply_fan_current_sensor_2 | AV80 | amperes |  | supply_fan_current_sensor_2 | amperes: amperes |  | N
AHU-24 | supply_fan_energy_accumulator_2 | AV81 | kilowatt_hours |  | supply_fan_energy_accumulator_2 | kilowatt_hours: kilowatt_hours |  | N
AHU-24 | supply_fan_power_sensor_2 | AV82 | kilowatts |  | supply_fan_power_sensor_2 | kilowatts: kilowatts |  | N
AHU-24 | supply_fan_run_time_accumulator_2 | AV83 | hours |  | supply_fan_run_time_accumulator_2 | hours: hours |  | N
AHU-24 | supply_fan_rotationalvelocity_sensor_2 | AV84 | revolutions_per_minute |  | supply_fan_rotationalvelocity_sensor_2 | revolutions_per_minute: revolutions_per_minute |  | N
AHU-24 | supply_fan_voltage_sensor_2 | AV85 | volts |  | supply_fan_voltage_sensor_2 | volts: volts |  | N
AHU-24 | supply_fan_current_sensor_3 | AV86 | amperes |  | supply_fan_current_sensor_3 | amperes: amperes |  | N
AHU-24 | supply_fan_energy_accumulator_3 | AV87 | kilowatt_hours |  | supply_fan_energy_accumulator_3 | kilowatt_hours: kilowatt_hours |  | N
AHU-24 | supply_fan_power_sensor_3 | AV88 | kilowatts |  | supply_fan_power_sensor_3 | kilowatts: kilowatts |  | N
AHU-24 | supply_fan_run_time_accumulator_3 | AV89 | hours |  | supply_fan_run_time_accumulator_3 | hours: hours |  | N
AHU-24 | supply_fan_rotationalvelocity_sensor_3 | AV90 | revolutions_per_minute |  | supply_fan_rotationalvelocity_sensor_3 | revolutions_per_minute: revolutions_per_minute |  | N
AHU-24 | supply_fan_voltage_sensor_3 | AV91 | volts |  | supply_fan_voltage_sensor_3 | volts: volts |  | N
AHU-24 | supply_fan_current_sensor_4 | AV92 | amperes |  | supply_fan_current_sensor_4 | amperes: amperes |  | N
AHU-24 | supply_fan_energy_accumulator_4 | AV93 | kilowatt_hours |  | supply_fan_energy_accumulator_4 | kilowatt_hours: kilowatt_hours |  | N
AHU-24 | supply_fan_power_sensor_4 | AV94 | kilowatts |  | supply_fan_power_sensor_4 | kilowatts: kilowatts |  | N
AHU-24 | supply_fan_run_time_accumulator_4 | AV95 | hours |  | supply_fan_run_time_accumulator_4 | hours: hours |  | N
AHU-24 | supply_fan_rotationalvelocity_sensor_4 | AV96 | revolutions_per_minute |  | supply_fan_rotationalvelocity_sensor_4 | revolutions_per_minute: revolutions_per_minute |  | N
AHU-24 | supply_fan_voltage_sensor_4 | AV97 | volts |  | supply_fan_voltage_sensor_4 | volts: volts |  | N
AHU-24 | return_air_relative_humidity_sensor | AV114 | percent_relative_humidity |  | return_air_relative_humidity_sensor | percent_relative_humidity: percent_relative_humidity |  | N
AHU-24 | return_air_temperature_sensor | AV7 | degrees_celsius |  | return_air_temperature_sensor | degrees_celsius: degrees_celsius |  | N
AHU-24 | supply_fan_speed_percentage_command | AV110 | percent |  |  |  |  | N
AHU-24 | supply_air_static_pressure_sensor | AV27 | pascals |  | supply_air_static_pressure_sensor | pascals: pascals |  | N
AHU-24 | supply_fan_run_status_1 | BV39 |  | 1=ON 0=OFF | supply_fan_run_status_1 |  |  | N
AHU-24 | supply_fan_run_status_2 | BV40 |  | 1=ON 0=OFF | supply_fan_run_status_2 |  |  | N
AHU-24 | supply_fan_run_status_3 | BV41 |  | 1=ON 0=OFF | supply_fan_run_status_3 |  |  | N
AHU-24 | supply_fan_run_status_4 | BV42 |  | 1=ON 0=OFF | supply_fan_run_status_4 |  |  | N
AHU-24 | filter_differential_pressure_status | BV6 |  | 1=PRESENT 0=ABSENT | filter_differential_pressure_status |  |  | N
AHU-24 | return_air_temperature_setpoint | AV12 | degrees_celsius |  | return_air_temperature_setpoint | degrees_celsius: degrees_celsius |  | N
AHU-24 | supply_air_static_pressure_setpoint | AV11 | pascals |  | supply_air_static_pressure_setpoint | pascals: pascals |  | N
AHU-23 | economizer_mode |  |  |  | economizer_mode |  |  | Y
AHU-23 | mixed_air_temperature_sensor |  |  |  | mixed_air_temperature_sensor |  |  | Y
AHU-23 | outside_air_damper_percentage_command |  |  |  | outside_air_damper_percentage_command |  |  | Y
AHU-23 | outside_air_temperature_sensor |  |  |  | outside_air_temperature_sensor |  |  | Y
AHU-23 | supply_air_temperature_setpoint |  |  |  | supply_air_temperature_setpoint |  |  | Y
AHU-24 | economizer_mode |  |  |  | economizer_mode |  |  | Y
AHU-24 | mixed_air_temperature_sensor |  |  |  | mixed_air_temperature_sensor |  |  | Y
AHU-24 | outside_air_damper_percentage_command |  |  |  | outside_air_damper_percentage_command |  |  | Y
AHU-24 | outside_air_temperature_sensor |  |  |  | outside_air_temperature_sensor |  |  | Y
AHU-24 | supply_air_temperature_setpoint |  |  |  | supply_air_temperature_setpoint |  |  | Y
AHU-24 | supply_fan_speed_percentage_command |  | percent |  | supply_fan_speed_percentage_command_1 | percent: percent |  | N
AHU-24 | supply_fan_speed_percentage_command |  | percent |  | supply_fan_speed_percentage_command_2 | percent: percent |  | N
AHU-24 | supply_fan_speed_percentage_command |  | percent |  | supply_fan_speed_percentage_command_3 | percent: percent |  | N
AHU-24 | supply_fan_speed_percentage_command |  | percent |  | supply_fan_speed_percentage_command_4 | percent: percent |  | N
AHU-24 | supply_fan_run_command_1 |  |  | 1=ON 0=OFF | supply_fan_run_command_1 |  |  | Y
AHU-24 | supply_fan_run_command_2 |  |  | 1=ON 0=OFF | supply_fan_run_command_2 |  |  | Y
AHU-24 | supply_fan_run_command_3 |  |  | 1=ON 0=OFF | supply_fan_run_command_3 |  |  | Y
AHU-24 | supply_fan_run_command_4 |  |  | 1=ON 0=OFF | supply_fan_run_command_4 |  |  | Y

## virtual_device_entities
virtual_points_type | device_points_type | dbo.source_device_field | dbo.virtual_device_field | dbo.abstracts

## asset_template
entity_instance_name | udmi.system.location.site | udmi.pointset.points | udmi.system.location.section | udmi.system.location.position.x | udmi.system.location.position.y | udmi.system.location.position.z | udmi.physical_tag.asset.guid | udmi.physical_tag.asset.site | udmi.physical_tag.asset.name | udmi.cloud.auth_type | dbo.devices_or_virtual_devices | dbo.type | dbo.connections.feeds | dbo.connections.controls | dbo.links | dbo.links.points | location | reporting_device